## 接口协议
接口协议
地址： 类型:POST 参数示例： { "time":"2021-05-08 15:00:00", "data":{ "ups":{ "input voltage":0.0, "input frequency":0.0, "output voltage":0.0, "output current":0.0, "output frequency":0.0, "output active power":0.0, "output apparent power":0.0, "load rate":0.0, "cabinet temperature":0.0, "battery voltage":0.0, "remaining battery capacity":0.0, "power on status":"开机完成", "power supply mode":"主路供电", "fault": true, "battery low voltage": true, "mains supply abnormality": true, }, "air conditioner":{ ...} ... } } |  |  | 响应示例 { “code”:””, "success": true, "message": “”, “data”:{ } "timestamp": 1620459538625 }
参数名 | 参数说明 | 类型 | 参数名 | 参数说明 | 类型
time | 上传时间戳 | String | success | 上传状态 | Boolean
input voltage | 输入电压 | number | message | 上传结果描述 | String
input frequency | 输入频率 | number | timestamp | 上传成功时间戳 | String
output voltage | 输出电压 | number | code | 处理结果code | String
output current | 输出电流 | number
output frequency | 输出频率 | number
output active power | 输出有功功率 | number
output apparent power | 输出视在功率 | number
load rate | 负载率 | number
cabinet temperature | 机柜温度 | number
battery voltage | 电池电压 | number
remaining battery capacity | 电池剩余容量 | number
power on status | 开机状态 | String
power supply mode | 供电模式 | String
fault | 故障 | bool
battery low voltage | 电池低压 | bool
mains supply abnormality | 市电异常 | bool
...
...

## 字段定义
id | 设备 | 参数 | 典型值 | 数据类型 | 单位
1 | ups | 输入电压/input_voltage | 220V | number | V
2 |  | 输入频率/input_frequency | 50Hz | number | Hz
3 |  | 输出电压/output_voltage | 220V | number | V
4 |  | 输出电流/output_current | 10A | number | A
5 |  | 输出频率/output_frequency | 50Hz | number | Hz
6 |  | 输出有功功率/output_active_power | 2kW | number | kW
7 |  | 输出视在功率/output_apparent_power | 2kVA | number | kVA
8 |  | 负载率/load_rate | 20% | number | %
9 |  | 机柜温度/cabinet_temperature | 25℃ | number | ℃
10 |  | 电池电压/battery_voltage | 108 | number | V
11 |  | 电池剩余容量/remaining_battery_capacity | 100% | number | %
12 |  | 开机状态/power_on_status | 开机完成 | String | /
13 |  | 供电模式/power_supply_mode | 主路供电 | String | /
14 |  | 故障/fault | FALSE | bool | /
15 |  | 电池低压/battery_low_voltage | FALSE | bool | /
16 |  | 市电异常/mains_supply_abnormality | FALSE | bool | /
17 | 空调/air_conditioner | 机柜温度/cabinet_temperature | 25℃ | number | ℃
18 |  | 送风温度/air_supply_temperature | 22℃ | number | ℃
19 |  | 电压/voltage | 220V | number | V
20 |  | 电流/current | 0.3A | number | A
21 |  | 压缩机状态/compressor_status | 运行 | String | /
22 |  | 内风机状态/Internal_fan_status | 运行 | String | /
23 |  | 外风机状态/external_fan_status | 运行 | String | /
24 |  | 加热状态/heating_state | 运行 | String | /
25 |  | 制冷告警/refrigeration_state | FALSE | bool | /
26 |  | 高温告警/high_temperature_alarm | FALSE | bool | /
27 |  | 低温告警/low_temperature_alarm | FALSE | bool | /
28 |  | 加热器故障/heater_fault | FALSE | bool | /
29 |  | 温度传感器故障/temperature_sensor_fault | FALSE | bool | /
30 |  | 高电压告警/high_voltage_alarm | FALSE | bool | /
31 |  | 低电压告警/low_voltage_alarm | FALSE | bool | /
32 |  | 制冷开启点/refrigeration_start_point | 28℃ | number | ℃
33 |  | 制冷灵敏点/refrigeration_sensitive_point | 3℃ | number | ℃
34 |  | 加热开启点/heating_start_point | 17℃ | number | ℃
35 |  | 加热灵敏点/heating_sensitive_point | 3℃ | number | ℃
36 |  | 高温告警点/high_temperature_alarm_point | 55℃ | number | ℃
37 |  | 低温告警点/low_temperature_alarm_point | 0℃ | number | ℃
38 | 烟雾传感器/smoke_sensor | 触发告警/trigger_alarm | FALSE | bool | /
39 | 水浸传感器/water_immersion_sensor | 触发告警/trigger_alarm | FALSE | bool | /
40 | 温湿度传感器/temperature_and_humidity_sensor | 当前温度/current_temperature | 25℃ | float | ℃
41 |  | 当前湿度/current_humidity | 55% | float | %
42 |  | 室温告警/room_temperature_alarm | FALSE | bool | /
43 |  | 湿度告警/humidity_alarm | FALSE | bool | /
44 | gps | 当前经度/current_longitude | 117.2312 | number | °
45 |  | 当前纬度/current_latitude | 31.934 | number | °
46 |  | 投放经度/launch_longitude | 117.2312 | number | °
47 |  | 投放纬度/launch_latitude | 31.934 | number | °
48 |  | 移位告警/shift_alarm | FALSE | number | /
49 | 太阳能控制器/solar_controller | 阵列电压/array_voltage | 44V | number | V
50 |  | 阵列电流/array_current | 1A | number | A
51 |  | 发电功率/generating_power | 44W | number | W
52 |  | 蓄电池电压/battery_voltage | 27V | number | V
53 |  | 蓄电池电流/battery_current | _-1.1A | number | A
54 |  | 最高电压/ceiling_voltage | 29.2V | number | V
55 |  | 最低电压/minimum_voltage | 26.34V | number | V
56 |  | 蓄电池温度/battery_temperature | 25℃ | number | ℃
57 |  | 蓄电池剩余电量/remaining_battery_capacity | 100% | number | %
58 |  | 负载电压/load_voltage | 27.6V | number | V
59 |  | 负载电流/load_current | 2.1A | number | A
60 |  | 负载功率/load_power | 53.4W | number | W
61 |  | 设备温度/equipment_temperature | 20℃ | number | ℃
62 |  | 当日累计用电量/accumulated_electricity_consumption_of_the_day | 1kW·H | number | kW·H
63 |  | 当月累计用电量/accumulated_electricity_consumption_of_the_current_month | 2kW·H | number | kW·H
64 |  | 当年累计用电量/accumulated_electricity_consumption_in_the_current_year | 3kW·H | number | kW·H
65 |  | 总累计用电量/total_accumulated_power_consumption | 4kW·H | number | kW·H
66 |  | 当日累计充电量/accumulated_charging_capacity_of_the_day | 5kW·H | number | kW·H
67 |  | 当月累计充电量/accumulated_charging_amount_of_the_current_month | 6kW·H | number | kW·H
68 |  | 当年累计充电量/accumulated_charging_capacity_of_the_current_year | 7kW·H | number | kW·H
69 |  | 总累计充电量/total_cumulative_charge | 8kW·H | number | kW·H
70 | 太阳能控制器2/solar_controller_2 | 阵列电压/array_voltage | 44V | number | V
71 |  | 阵列电流/array_current | 1A | number | A
72 |  | 发电功率/generating_power | 44W | number | W
73 |  | 蓄电池电压/battery_voltage | 27V | number | V
74 |  | 蓄电池电流/battery_current | _-1.1A | number | A
75 |  | 最高电压/ceiling_voltage | 29.2V | number | V
76 |  | 最低电压/minimum_voltage | 26.34V | number | V
77 |  | 蓄电池温度/battery_temperature | 25℃ | number | ℃
78 |  | 蓄电池剩余电量/remaining_battery_capacity | 100% | number | %
79 |  | 负载电压/load_voltage | 27.6V | number | V
80 |  | 负载电流/load_current | 2.1A | number | A
81 |  | 负载功率/load_power | 53.4W | number | W
82 |  | 设备温度/equipment_temperature | 20℃ | number | ℃
83 |  | 当日累计用电量/accumulated_electricity_consumption_of_the_day | 1kW·H | number | kW·H
84 |  | 当月累计用电量/accumulated_electricity_consumption_of_the_current_month | 2kW·H | number | kW·H
85 |  | 当年累计用电量/accumulated_electricity_consumption_in_the_current_year | 3kW·H | number | kW·H
86 |  | 总累计用电量/total_accumulated_power_consumption | 4kW·H | number | kW·H
87 |  | 当日累计充电量/accumulated_charging_capacity_of_the_day | 5kW·H | number | kW·H
88 |  | 当月累计充电量/accumulated_charging_amount_of_the_current_month | 6kW·H | number | kW·H
89 |  | 当年累计充电量/accumulated_charging_capacity_of_the_current_year | 7kW·H | number | kW·H
90 |  | 总累计充电量/total_cumulative_charge | 8kW·H | number | kW·H